# QiO Foresight Edge

# Customer Remote Access & Edge Readiness Guide

Prerequisite guide for onsite teams

Prepared date: 29 April 2026

Contents

1. Purpose and outcome	3

2. Prepare the edge device	3

2.1 QiO-supplied edge device	3

2.2 Customer-supplied device	3

3. Connect the two networks	4

4. Confirm basic connectivity	4

5. Give QiO remote access	5

5.1 Preferred: QiO-provided DWAgent access	5

5.2 Customer-approved tools or VPN	5

6. Final readiness checklist	5

7. Appendix – DWAgent Installation Instructions	6

# Purpose and outcome

This guide explains what the customer needs to prepare before QiO installs the Foresight Edge application. The aim is simple: provide the right edge device, connect it to the internet and the PLC/SCADA network, and give QiO approved remote access. QiO will complete the application, VPN, data collection, and validation work after access is available.

Success looks like this: QiO can remotely access the edge device, confirm the internet and PLC network connections, and start installation without further customer-side setup.

# Prepare the edge device

## QiO-supplied edge device

Instruction: Place the device near the control cabinet or network panel, connect power, connect one LAN port to the approved internet/remote-access network, and connect the second LAN port to the approved PLC/SCADA network.

No customer software installation is normally required on a QiO-supplied device.

Label the two cables clearly: Internet / Remote Access and PLC / SCADA.

Keep the device powered on during the agreed access window.

## Customer-supplied device

Instruction: Provide a PC, industrial PC, or server-class workstation that customer IT can support and patch. Windows is preferred when that is the fastest customer-supported route; Linux can be used as well if agreed with customer IT.

Preferred memory: 16 GB RAM. Lower RAM may be acceptable by agreement for small pilots.

Preferred storage: 200 GB available disk. Increase this if longer local data storage is required.

Network: two LAN ports or two separate network adapters are required.

Access: a temporary local administrator route, service account, or supervised installation window is required.

Why this matters: Two separate network connections let QiO read PLC/SCADA data while keeping the internet/remote-access path separate from the control network. Local storage is used for buffering data if cloud back-up is not opted.

# Connect the two networks

Instruction: Use one connection for internet/remote access and one connection for PLC/SCADA access. Do not bridge, share, or route traffic between these two networks.

- Connect LAN 1 to the approved internet or remote-access network.

- Connect LAN 2 to the approved PLC, SCADA, OPC, or industrial-control network.

- Confirm LAN 1 has a valid IP address for the internet/remote-access network.

- Confirm LAN 2 has a valid IP address on the same network as the PLC/OPC endpoint that QiO will read.

- Confirm customer IT/OT has not enabled routing, bridging, or internet sharing between LAN 1 and LAN 2.

Why this matters: QiO needs remote access to the edge device and read access to the PLC/SCADA data source. The edge device should not act as a route between the internet and the control network.

# Confirm basic connectivity

Instruction: Run these checks before the QiO installation session or have the customer IT/OT contact ready to run them with QiO during the session.

- Internet side: confirm the device can open the approved remote-access tool or customer VPN route.

- PLC side: confirm the device can reach the approved PLC, SCADA, OPC, or gateway IP address from the PLC network adapter.

- IP check: record the IP address of each adapter and which network each adapter is connected to.

- Security check: confirm the firewall allows the agreed remote-access method and any customer-approved cloud/VPN destinations.

Good outcome: the internet connection works, the PLC/SCADA connection reaches the approved endpoint, and QiO can verify that the two network paths remain separate.

# Give QiO remote access

## Preferred: QiO-provided DWAgent access

Instruction: QiO will provide a DWAgent installation script or installer and an installation code. Run it on the edge device during the agreed setup window. When prompted, use the installation code provided by QiO.

- Download or copy the QiO-provided DWAgent installer or script onto the edge device:

- For windows: https://www.dwservice.net/download/dwagent_x86.exe

- For other OS devices: https://www.dwservice.net/en/download.html

- Run the installer or script using the customer-approved administrator process. Please refer to the appendix for step by step instructions on DWAgent installtions.

- Enter the QiO-provided installation code when prompted.

- Tell QiO when the agent is installed and the device is online.

Why this matters: This gives QiO a controlled remote session so QiO can install the VPN, configure the application, validate the PLC/SCADA connection, and troubleshoot without requiring a separate onsite approval route.

## Customer-approved tools or VPN

Instruction: If customer IT prefers another approved method, QiO can support it. Examples include customer VPN, jump host, Remote Desktop through an approved gateway, TeamViewer, AnyDesk, UltraViewer, NoMachine, RustDesk, or a similar customer-approved remote-support tool.

Send QiO the following information through the customer-approved secure channel:

Remote method name, device name, site name, and agreed access window with timezone.

Session link, connection ID, VPN/jump-host details, or other connection reference.

Temporary password, one-time code, or MFA approval contact, if required by customer policy.

Name, phone number, and email of the customer IT/OT contact who can approve access or assist during installation.

# Final readiness checklist

Edge device is powered on and located near the required network connections.

Internet/remote-access LAN and PLC/SCADA LAN are connected to the correct ports and clearly labelled.

Both adapters have valid IP addresses for their respective networks.

The PLC, SCADA, OPC, or gateway endpoint is reachable from the PLC-side adapter.

Remote access is installed, enabled, and shared with QiO for the agreed window.

A customer IT/OT contact is available for firewall, VPN, MFA, or PLC network questions.

Once these items are complete, QiO can remote in and complete the Foresight Edge application installation and validation.

# Appendix – DWAgent Installation Instructions

Download the Agent installer for your device from our download page (https://www.dwservice.net/download.html).

After downloading the file, open it to start the installation process.

A wizard will be launched to guide you through the installation.

  - From the options, select Install.

  - Click on the Next button.

Here you can see the location where the Agent will be installed. This is the default path.

  - If you want to install the Agent somewhere else, you can change the path here.

  - Click on the Next button.

The next page of the wizard is displayed:

  - Select Yes to confirm that the specified installation path is correct.

  - Click on the Next button.

The next page of the wizard is displayed:

  - From the two installation modes, select the ‘Enter the installation code‘ option.

  - Click on the Next button.

The next page of the wizard is displayed:

  - In this field, enter your Installation code. This is the 9 digit code that the QiO generated for this particular installation.

  - Click on the Next button.

After installation, the Monitor icon appears in the taskbar.

Click on the Monitor icon to show the DWAgent – Monitor window.